## Population Data
CIGRE WG A2-37: RELIABILITY QUESTIONNAIRE
This questionnaire applies to all AC power transformers and reactors with highest system voltage ≥ 60kV.
1.1. | REFERENCE YEAR/PERIOD
1.2. | FAILURE DATA LIMITATIONS
2 | UTILITY INFORMATION
Country
Utility Name
Mailing Address
Contact Person
Telephone Number
Fax Number
Email Address
Identifier
3 | POPULATION INFORMATION | HIGHEST SYSTEM VOLTAGE [kV]
|  | 69 ≤ U < 100 | 100 ≤ U < 200 | 200 ≤ U < 300 | 300 ≤ U < 500 | 500 ≤ U < 700 | U ≥ 700
Complete 3.1 and 3.2 below OR provide the installed population information for the indicated reference year, as per standard utility format.
Please indicate the number of units per voltage category in operation during the reference period.
3.1. | Application
Substation - Distribution
Substation - Transmission
Power Station - Generator Step-Up
Power Station - Unit Transformer
Shunt Reactor
Other: Please specify
3.2. | Type
Two Winding
Two Winding with Tertiary
Autotransformer
Autotransformer with Tertiary
3.3. | Number of Phases In Tank
1 - Phase
3 - Phases
Please indicate the voltage ratios, rated power, typical loading and manfacturing period per voltage category.
3.4. | Voltage Ratios
Substation - Distribution
Substation - Transmission
Power Station - Generator Step-Up
Power Station - Unit Transformer
Other: Please specify
3.5. | Rated Power
Substation - Distribution
Substation - Transmission
Power Station - Generator Step-Up
Power Station - Unit Transformer
Shunt Reactor
Other: Please specify
3.6. | Typical Loading
Substation - Distribution
Substation - Transmission
Power Station - Generator Step-Up
Power Station - Unit Transformer
Other: Please specify
3.7. | Typical Manufacturing Period
Please indicate the average age of the population in the respective application. You may submit this information by individual documentation.
Substation - Distribution
Substation - Transmission
Power Station - Generator Step-Up
Power Station - Unit Transformer
Shunt Reactor
Other: Please specify
4 | DEFINITIONS
Please describe how a transformer and reactor failure is defined by your utility.
5 | FAILURE DATA COLLECTION
Please describe how transformer and reactor failure data are collected in your utility.You may submit any supporting documentation.
Note on B5: Ten: Please indicate period in which the failures happened. Please include ALL major failures of this period. The period should not be shorter than 5 years.
Note on B7: If not all voltage classes are included in this failure data record, please indicate here! Example: If only failures of transformers with nominal voltage greater than 110 kV were collected, then write: Only failures of transformers with voltages greater than 110kV are given.
Note on B18: tenbo: Identifier is given by WG A2.37 internally in order to anonymize data!

## Failure Data
This survey should cover major failures only!
| 1 - IDENTIFICATION OF THE UNIT |  |  |  | 2 - FEATURES OF THE UNIT | [8 empty] | 3 - DETAIL OF OCCURENCE |  |  | 4 - CONSEQUENCES OF FAILURE | [6 empty] | 5 - REMARKS, Internal Identification, Repair History
No. | 1.1 | 1.2 | 1.3 | 1.4 | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 3.1 | 3.2 | 3.3 | 4.1 | 4.2 | 4.3 | 4.4 | 4.5 | 4.6 | 4.7
| Application | Type | Construction Type | Year of Manufacture | Rated Power [MVA] | Nominal Voltage [kV] | Number of Phases | Cooling System | Type of Oil | Tap Changer | Tap Changer Arrangement | Oil Preservation System | Over Voltage Protection | Year of Failure | Service Years to Failure | Loading Immediately Prior to Failure | External Effects | Failure Location | Service Years of Failed Bushings in 4.2 | Failure Mode | Failure Cause | Action | Detection Mode
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
Note on A1: Major Failure: Any situation which requires the equipment to be removed from service for a period longer than 7 days for investigation, remedial work or replacement. Where repairs are required, these involve major remedial work, usually requiring the transformer to be removed from its plinth and returned to the factory. A major failure would require at least the opening of the tank, including the tap changer tank or an exchange of bushings. Also a reliable indication that the condition of the transformer prevents a safe operation, should be counted as a major failure if remedial work (longer than 7 days) is needed for restoring original service capability (e.g. detection of strong PDs). If the transformer is therefore not put into operation, indicate in field 3.3 "0 p.u. (switched off)".
Note on Y3: Eskom: Indicate the total number of previous repairs (due to major failures) per transformer. Also indicate the year that each transformer went for repairs.
Note on N4: Internal surge Arrester means internal line arresters, internal part winding varistors, diverter switch internal varistors
Note on Q4: Select 0 pu (switched off), if removal from service is based on decision that transformer is defective. Select 0 pu (switched on), if transformer failed during energizing or no load operation.
Note on R4: Select the most severe effect.
Note on S4: Identify the primary location (component) in the transformer where the failure was initiated.
Note on T4: Eskom: If the answer to 4.2 is bushings then indicate the number of service years of the failed bushing. With bushing replacement the bushing service years to failure often differs from the transformer's service years to failure.
Note on U4: A description of the nature of the failure illustrating what actually happened when the failure occurred. Give the failure mode of the failure location (component) where the failure was initiated. The definitions are according to Cigre Brochure 227, page 69. Dielectric Failure means PD, tracking, flashover. Electrical failure means open circuit, short circuit, poor joint, poor contact, ground deterioration, floating potential.
Note on V4: The circumstances during design, manufacture or application that led to the failure. Give the failure cause of the failure location (component) where the failure was initiated.
Note on X4: tenbo: How was the failure detected?

## Answers
1- IDENTIFICATION OF THE UNIT
1.1 Application
Substation - Distribution
Substation - Transmission
Power Station - Generator Step-Up
Power Station - Unit Transformer
HVDC - Transformer
Shunt Reactor
Other: Please specify
1.2 Type
Two Winding
Two Winding with Tertiary
Autotransformer
Autotransformer with Tertiary
1.3 Construction Type
Core Type
Shell Type
2 - FEATURES OF THE UNIT
2.3 Number of Phases
Single Phase
Three Phase
2.4 Cooling System
ONAN
ONAF
OFAF
ODAF
OFWF
ODWF
2.5 Type of Oil
Mineral Oil
Natural Ester
Synthetic Ester
Gas (SF6)
Other
2.6 Tap Changer
On-Load Tap-Changer (oil breaker)
On-Load Tap-Changer (vacuum breaker)
Off-Circuit Tap-Changer (OCTC)
Without Tap Changer
2.7 Tap Changer Arrangement
Tap selector in main tank oil, seperate compartment for diverter switch
Combined tap selector and diverter switch in main tank oil
Combined tap selector and diverter switch in seperate compartment from main tank
Seperate compartments for both tap selector and diverter switch
Off circuit
None
2.8 Oil Preservation System
Sealed
Free breathing
Nitrogen blanket
2.9 Over Voltage Protection
Spark gaps
External Surge arresters
Internal Surge arresters
Internal and External Surge arresters
None
3 - DETAIL OF OCCURENCE
3.3 Loading Immediately Prior to Failure
0 pu (switched off)
0 pu (switched on)
< 0,5 pu
0,5 - 0,8 pu
0.8 - 1 pu
> 1 pu
Variable
Not known
4 - CONSEQUENCES OF FAILURE
4.1 External Effects
None
Leakages
Explosion, Burst
Fire
Collateral Damages
Others
4.2 Failure Location
HV Winding
MV Winding
LV Winding
Tapping Winding
HV Lead Exit
MV Lead Exit
LV Lead Exit
Phase to Phase Insulation
Winding to Ground Insulation
Winding to Winding Insulation
Electrical Screen
HV Bushings
MV Bushings
LV Bushings
Neutral Bushings
Core and magnetic circuit
Flux Shunts
Tank
Cooling unit
Tap Changer
CT
Unknown
4.4 Failure Mode
Dielectric
Electrical
Thermal
Physical chemistry (including oil, corrosion, contamination etc)
Mechanical
Unknown
4.5 Failure Cause
Improper Transformer Specification
Design
Manufacturing
Material
Corrosive Sulphur
Transport, Handling or Storage
Loss of clamping pressure
Installation on-site
Improper maintenance
Improper repair
Abnormal Overload
Overvoltage
Overheating
Lightning
External short-circuit
Repetitive through faults
Seismic Disturbances
Improper application
External Pollution
Loss of cooling
Vandalism
Abnormal Deterioration
Aging
Collateral Damage
Other reasons
Unknown
4.6 Action
Onsite Repair < 1 week
Onsite Repair > 1 week
Onsite Repair > 1 month
Repair in workshop
Scrapping
Unknown
4.7 Detection Mode
Overcurrent relay
Differential protection relay
Buchholz relay
Pressure relief device
DGA
other diagnostics
Unknown

## Definitions
Definitions, Remarks
This survey should cover major failures only!
| Failure | Any unscheduled situation which requires the equipment to be removed from service for investigation, remedial work or replacement. Failure can be divided into minor and mayor failures both with forced and scheduled outages.
| Major Failure | Any situation which requires the equipment to be removed from service for a period longer than 7 days for investigation, remedial work or replacement. Where repairs are required, these involve major remedial work, usually requiring the transformer to be removed from its plinth and returned to the factory. A major failure would require at least the opening of the tank, including the tap changer tank or an exchange of bushings. Also a reliable indication that the condition of the transformer prevents a safe operation, should be counted as a major failure if remedial work (longer than 7 days) is needed for restoring original service capability (e.g. detection of strong PDs). If the transformer is therefore not put into operation, indicate in field 3.3 "0 p.u. (switched off)".
| Minor Failure | A minor failure require remedial work that lasts shorter than 7 days.
Population Data:
1 | Reference Period | Please indicate the period, in which the failures happend. Minimum period is 5 years. Please include ALL major failures of this period.
Failure Data:
1 - Identification of the Unit
2 - Features of the Unit
2.7 | Tap Changer Arrangement
2.9 | Over Voltage Protection | Internal surge Arrester means internal line arresters, internal part winding varistors, diverter switch internal varistors
3 - Detail of Occurence
3.3 | Loading Immediately Prior to Failure | Select 0 pu (switched off), if removal from service is based on decision that transformer is defective. Select 0 pu (switched on), if transformer failed during energizing or no load operation.
4 - Consequences of Failure
4.1 | External Effects | Select the most severe effect.
4.2 | Failure Location | Identify the primary location (component) in the transformer where the failure was initiated.
4.3 | Service Years to Failure of Bushings in 4.2 | If the answer to 4.2 is bushings the indicate the number of service years of the failed bushing.With bushing replacement the bushing service years to failure often differs from the transformer's service years to failure.
4.4 | Failure Mode | A description of the nature of the failure illustrating what actually happened when the failure occurred. Give the failure mode of the failure location (component) where the failure was initiated. The definitions are according to Cigre Brochure 227, page 69. Dielectric Failure means PD, tracking, flashover. Electrical failure means open circuit, short circuit, poor joint, poor contact, ground deterioration, floating potential.
4.5 | Failure Cause | The circumstances during design, manufacture or application that led to the failure. Give the failure cause of the failure location (component) where the failure was initiated. If an animal caused an external flashover, which led to a major failure (e.g. mechanical displacement of LV winding), give "external pollution" as failure cause.
5 - REMARKS, Internal Identification, Repair History
Indicate the total number of previous repairs (due to major failures) per transformer. Also indicate the year that each transformer went for repairs.