## Definitions
Definitions, Remarks
This survey should cover major failures only!
| Failure | Any unscheduled situation which requires the equipment to be removed from service for investigation, remedial work or replacement. Failure can be divided into minor and major failures both with forced and scheduled outages.
| Major Failure | Any situation triggered by a tripping which requires the equipment to be removed from service for a period longer than 7 days for investigation, remedial work or replacement. Where repairs are required, these involve major remedial work, usually requiring the transformer to be removed from its plinth and returned to the factory. A major failure would require at least the opening of the tank, including the tap changer tank or an exchange of bushings.
| Minor Failure | A minor failure requires remedial work that lasts shorter than 7 days. Minor failures are not counted in this questionnaire!
| Retirement due to condition/age | Transformer is retired/scrapped after detection of a condition that prevents safe or reliable operation (e.g. bad DGA or partial discharges); controlled outage (without tripping event) combined with scrapping.
| Retirement due to network requirements | Transformer is retired/scrapped because network requires new characteristics (e.g. different voltage level, rating, losses, noises)
Population Data:
1 | Reference Period | Please indicate the period, in which the failures happend. Minimum period is 5 years. Please include ALL retirements and major failures of this period.
Failure Data:
1 - Identification of the Unit
2 - Features of the Unit
2.4 | Cooling System | Cooling System for highest rating of unit
3 - Detail of Occurence
4 - Consequences of Failure
4.1 | External Effects | Select the most severe effect.
4.2 | Failure Location | Identify the primary location (component) in the transformer where the failure was initiated.
4.3 | Failure Mode | A description of the nature of the failure illustrating what actually happened when the failure occurred. Give the failure mode of the failure location (component) where the failure was initiated. The definitions are according to Cigre Brochure 227, page 69. Dielectric Failure means PD, tracking, or flashover. Electrical failure means open circuit, short circuit, poor joint, poor contact, ground deterioration, or floating potential.
4.4 | Failure Cause | Give the failure cause of the failure location (component) where the failure was initiated. If an animal caused an external flashover, which led to a major failure (e.g. mechanical displacement of LV winding), give "external pollution" as failure cause.
4.6 | Detection Mode | Please give detection mode which triggered first.
5 - REMARKS, Internal Identification, Repair History
Indicate the total number of previous repairs per transformer. Also indicate the year that each transformer was repaired. Please also indicate, if problem occurred also to other units of that family.

## Population Data
CIGRE WG A2-62: RELIABILITY QUESTIONNAIRE (Ver. 4)
Collection of Retirements and Major Failures
This questionnaire applies to all AC power transformers and reactors with highest system voltage ≥ 100kV.
1.1. | REFERENCE YEAR/PERIOD
1.2. | FAILURE DATA LIMITATIONS
2 | UTILITY INFORMATION
Country
Utility Name
Mailing Address
Contact Person
Telephone Number
Fax Number
Email Address
Identifier
3 | POPULATION INFORMATION (Number of transformers)
|  | 100 ≤ U < 200 | 200 ≤ U < 300 | 300 ≤ U < 500 | 500 ≤ U < 700 | U ≥ 700
Complete 3.1 for the indicated reference period OR provide the installed population information in the age distribution sheet.
Please indicate the number of units per voltage category in operation during the reference period.
3.1. | Application
Substation
GSU - Thermal
GSU - Hydro
GSU - Wind
GSU - PV
Shunt Reactor
Note on B5: Ten: Please indicate period in which the failures and retirements happened. Please include ALL retirements and major failures of this period. The period should not be shorter than 5 years, preferably 2010-2019.
Note on B7: If not all voltage classes are included in the failure + retirement data sheet, please indicate here! Example: If only failures of transformers with nominal voltage of 100..200 kV were collected, although the population consists of voltage higher 200 kV, then write: Only failures of transformers with voltages between 100 and 200 kV are given.
Note on B18: tenbo: Identifier is given by WG A2.62 internally in order to anonymize data

## Age Distribution
Year of Commissioning | Number of Transformers
| 100 ≤ U < 200 | 200 ≤ U < 300 | 300 ≤ U < 500 | 500 ≤ U < 700 | U ≥ 700
2019
2018
2017
2016
2015
2014
2013
2012
2011
2010
2009
2008
2007
2006
2005
2004
2003
2002
2001
2000
1999
1998
1997
1996
1995
1994
1993
1992
1991
1990
1989
1988
1987
1986
1985
1984
1983
1982
1981
1980
1979
1978
1977
1976
1975
1974
1973
1972
1971
1970
1969
1968
1967
1966
1965
1964
1963
1962
1961
1960
1959
1958
1957
1956
1955
1954
1953
1952
1951
1950

## Failure + Retirement Data
This survey should cover retirements and major failures only!
| 1 - IDENTIFICATION OF THE UNIT |  | 2 - FEATURES OF THE UNIT | [5 empty] | 3 - DETAIL OF OCCURENCE |  |  | 4 - CONSEQUENCES OF FAILURE | [5 empty] | 5 - REMARKS, Internal Identification, Repair History
No. | 1.1 | 1.2 | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 3.1 | 3.2 | 3.3 | 4.1 | 4.2 | 4.3 | 4.4 | 4.5 | 4.6
| Application | Year of Manufacture | Rated Power [MVA] | Nominal Voltage [kV] | Number of Phases | Cooling System | Type of Tap Changer | Type of Bushing | Year of Failure | Service Years to Failure | Reason for Disconnection (Retirement or Failure) | External Effects | Failure Location | Failure Mode | Failure Cause | Action | Detection Mode
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
Note on A1: Major Failure: Any situation which requires the equipment to be removed from service for a period longer than 7 days for investigation, remedial work or replacement. Where repairs are required, these involve major remedial work, usually requiring the transformer to be removed from its plinth and returned to the factory. A major failure would require at least the opening of the tank, including the tap changer tank or an exchange of bushings. Also a reliable indication that the condition of the transformer prevents a safe operation, should be counted as a major failure if remedial work (longer than 7 days) is needed for restoring original service capability (e.g. detection of strong PDs). If the transformer is therefore not put into operation, indicate in field 3.3 "0 p.u. (switched off)".
Note on S3: Eskom: Indicate the total number of previous repairs (due to major failures) per transformer. Also indicate the year that each transformer went for repairs.
Note on M4: Select the most severe effect.
Note on N4: Identify the primary location (component) in the transformer where the failure was initiated.
Note on O4: A description of the nature of the failure illustrating what actually happened when the failure occurred. Give the failure mode of the failure location (component) where the failure was initiated. The definitions are according to Cigre Brochure 227, page 69. Dielectric Failure means PD, tracking, flashover. Electrical failure means open circuit, short circuit, poor joint, poor contact, ground deterioration, floating potential.
Note on P4: Give the failure cause of the failure location (component) where the failure was initiated.
Note on R4: Please give detection mode which triggered first.

## Answers (hidden)
1- IDENTIFICATION OF THE UNIT
1.1 Application
Substation
GSU - Thermal
GSU - Hydro
GSU - Wind
GSU - PV
Shunt Reactor
2 - FEATURES OF THE UNIT
2.3 Number of Phases
Single Phase
Three Phase
2.4 Cooling System
ONAN
ONAF
OFAF
ODAF
OFWF
ODWF
Type of Oil
Mineral Oil
Natural Ester
Synthetic Ester
Gas (SF6)
Other
2.5 Type of Tap Changer
On-Load Tap-Changer
Off-Circuit Tap-Changer (OCTC)
Without Tap Changer
2.6 Type of HV Bushing
Oil Impregnated Paper (OIP)
Resin Impregnated Paper (RIP)
Resin Impreganted Synthetic (RIS)
Oil SF6 bushing
Cable Box
unknown
3 - DETAIL OF OCCURENCE
3.3 Reason for Disconnection
Retirement due to network requirements
Retirement due to condition/age (w/o tripping)
Major Failure (with tripping)
4 - CONSEQUENCES OF FAILURE
4.1 External Effects
None
Leakage only
Fire
Explosion w/o fire
Explosion with fire
4.2 Failure Location
Winding
Tapping Winding
Lead Exit
Tapping Leads
Phase to Phase Insulation
Winding to Ground Insulation
Winding to Winding Insulation
Electrical Screen
Bushings
Core and magnetic circuit incl. clamping
Flux Shunts
Tank, Conservator, Piping
Cooling unit, Pump, Fan, Radiator
Tap Changer
Internal Surge Arresters
CT
Unknown
4.3 Failure Mode
Dielectric
Electrical
Thermal
Physical chemistry (including oil, corrosion, contamination etc)
Mechanical
Unknown
4.4 Failure Cause
Transport, Handling or Storage
Installation on-site
Improper maintenance or repair
Paper ageing
Overload
Overvoltage, Lightning
Overheating
Corrosive Sulphur
Oil Quality
External short-circuit
Geomagnetic Induced Currents
Seismic Disturbances
External Pollution
Loss of cooling
Loss of clamping pressure
Collateral Damage
Vandalism
Material
Other reasons
Unknown
4.5 Action
Onsite Repair < 1 week
Onsite Repair > 1 week
Onsite Repair > 1 month
Repair in workshop
Scrapping
Unknown
4.6 Detection Mode
Site Inspection
Online Monitoringsystem
Laboratory DGA, Oil Quality Test
Other offline Diagnostics
Overcurrent relay
Differential protection relay
Buchholz relay
Pressure relief device
Unknown